## outdoor unit
Model |  |  | AL-H18/4DR1(U) | AL-H24/4DR1(U) | AL-H36/4DR1(U) | AL-H48/5DR1(U) | AL-H60/5DR1(U)
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3
Max. Input Consumption |  | W | 2400 | 3470 | 4360 | 7300 | 7700
Max. Current |  | A | 12.1212 | 17.5253 | 19.8 | 12.3239 | 12.9992
Capacity | Cooling | Btu/h | 20000-18000-5500 | 26500-24000-7200 | 40000-36000-10800 | 51800-48000-14400 | 63000-60000-18000
|  | W | 5610-5100-1530 | 7920-7200-2160 | 11000-10000-3000 | 15120-14000-4200 | 16800-16000-4800
| Heating | Btu/h | 20140-19000-4750 | 29700-27000-6750 | 43125-37500-11250 | 56100-51000-17850 | 69300-63000-22050
|  | W | 5936-5600-1400 | 8690-7900-1975 | 13225-11500-3450 | 17050-15500-5425 | 19800-18000-6300
DC Inverter Compressor | Model |  | ATD141RDPA8JTA | ATL232UDPC9AQ | DA250S2C-30MT | ATQ420D2UMU | ATQ420D2UMU
| Type |  | ROTARY | ROTARY | ROTARY | ROTARY | ROTARY
| Brand |  | Shanghai Hitachi | Shanghai Hitachi | GMCC | GMCC | GMCC
| Capacity | W | 5560 | 6520 | 7690 | 13100 | 13100
| Input | W | 1255 | 2070 | 2120 | 3420 | 3420
| Frequency range | Hz | 16.7-120 | 20-240 | 12-120 | 12-120 | 12-120
| Rated Current(RLA) | A | 4.2 | 8.8 | 8.85 | 6.9 | 6.9
| Locked Rotor Amp(LRA) | A | 30 | 32 | 45 | 44 | 44
| Refrigerant Oil | ml | 480 (68HES-H) | 630 (HAF68D1C) | 820 (ESTER OIL VG74) | 1400 (POE VG74) | 1400 (POE VG74)
Outdoor Fan Motor | Model |  | CW65A | CW70A | YDK120-6 | WC55-6 | WC55-6
| Brand |  | weiling | AUX/weiling | Weiling | weiling | weiling
| Output Power x Fan quantity | W | 65×1 | 70×1 | 120×1 | 55×2 | 55×2
| Capacitor | uF | 4 | 4 | 5 | 3×2 | 3×2
| Speed | r/min | 830/710/550 | 830/700/500 | 830/720/620 | 780/660/530 | 780/660/530
Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2
| b.Tube Pitch(a)x Row Pitch(b) | mm | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05
| c.Fin Pitch | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.And Material | mm | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
| f.Coil Length x Height x Width | mm | 736×550×38.1 | 740×660×38.1 | 836×761×38.1 | 954×1320×38.1 | 954×1320×38.1
| g.Heat Exchanging Area | ㎡ | 16.92 | 21.26 | 27.23 | 54.84 | 54.84
Air Flow Volume |  | CFM | 1529.4118 | 1647.0588 | 2294.1176 | 3764.7059 | 3764.7059
|  | m3/h | 2600 | 2800 | 3900 | 6400 | 6400
Noise Level |  | dB(A) | 55 | 60 | 60 | 56 | 56
Dimension(W×D×H) | Net | mm | 800×300×590 | 800×300×690 | 900×320×790 | 940×368×1366 | 940×368×1366
| Packing | mm | 930×410×660 | 930×410×760 | 1030×430×850 | 1080×460×1500 | 1080×460×1500
Weight | Net | kg | 45 | 56 | 62 | 110 | 110
| Gross | kg | 49 | 60 | 67 | 118 | 118
Refrigerant Type/Quantity | Type |  | R410A | R410A | R410A | R410A | R410A
| Charged Volume | kg | 1.3 | 1.7 | 1.9 | 3.7 | 3.7
Design Pressure |  | MPa | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Refrigerant Piping | Liquid Side | mm | 6.35(1/4) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8)
| Gas Side | mm | 12.7(1/2) | 15.88(5/8) | 15.88(5/8) | 19.05(3/4) | 19.05(3/4)
| Drainage | mm | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20)
| Max. Length | m | 20 | 30 | 30 | 50 | 50
| Max. Height | m | 15 | 15 | 20 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24
Connection Wiring | Power Wiring（Indoor） | mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm3 | 3×1mm3
| Power Wiring（Outdoor） | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×2.5mm2 | 5×1.5mm3 | 5×1.5mm3
| Signal Wiring | mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Stuffing Quantity | 20/40/40H | Unit | 102/204/272 | 102/204/204 | 56/112/168 | 27/54/54 | 27/54/54

## R410a-T1-50Hz(Ca)
Model | Indoor |  | ALCA-H18/4DR1 | ALCA-H24/4DR1 | ALCA-H36/4DR1 | ALCA-H48/5DR1 | ALCA-H60/5DR1
| Panel |  | MB13 | MB12 | MB12 | MB12 | MB12
| Outdoor |  | AL-H18/4DR1(U) | AL-H24/4DR1(U) | AL-H36/4DR1(U) | AL-H48/5DR1(U) | AL-H60/5DR1(U)
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3
Capacity | Cooling | Btu/h | 20000-18000-5500 | 26500-24000-7200 | 40000-36000-10800 | 51800-48000-14400 | 63000-60000-18000
|  | W | 5610-5100-1530 | 7920-7200-2160 | 11000-10000-3000 | 15120-14000-4200 | 16800-16000-4800
| Heating | Btu/h | 20140-19000-4750 | 29700-27000-6750 | 43125-37500-11250 | 56100-51000-17850 | 69300-63000-22050
|  | W | 5936-5600-1400 | 8690-7900-1975 | 13225-11500-3450 | 17050-15500-5425 | 19800-18000-6300
Electric Data | Rated Cooling Power Input | W | 2053-1579-474 | 2880-2215-665 | 4012-3086-926 | 5582-4294-1288 | 6479-4984-1495
| Rated Heating Power Input | W | 2011-1547-464 | 2813-2164-649 | 4118-3168-950 | 5461-4201-1260 | 6429-4945-1484
| Rated Cooling Current | A | 9.81-7.55-2.25 | 13.78-10.60-3.21 | 19.19-14.77-4.45 | 9.84-7.57-2.27 | 11.18-8.60-2.57
| Rated Heating Current | A | 9.62-7.40-2.20 | 13.44-10.36-3.11 | 19.71-15.16-4.55 | 9.68-7.45-2.23 | 10.95-8.42-2.54
Performance | EER | W/W | 3.23 | 3.25 | 3.24 | 3.26 | 3.21
| COP | W/W | 3.62 | 3.65 | 3.63 | 3.69 | 3.64
Indoor Fan Motor | Model |  | YDK30-6E1 | XD30A | YDK45-6 Q | XD80A | XD80A
| Brand |  | Sinjun | Sinjun | Sinjun | Sinjun | Sinjun
| Output Power x Fan quantity | W | 30×1 | 30×1 | 45×1 | 80×1 | 80×1
| Capacitor | uF | 2.5 | 3 | 4 | 6 | 6
| Speed (Hi/Mi/Lo) | r/min | 920/850/750 | 500/430/320 | 650/520/450 | 695/585/495 | 695/585/495
Indoor Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Pitch | mm | 1.5 | 1.6 | 1.4 | 1.4 | 1.4
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.and Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 1160×184.5×25.4 | 2014×205×25.4 | 2014×205×25.4 | 2014×246×25.4 | 2014×246×25.4
| g.Heat Exchanging Area | m2 | 5.76 | 9.43 | 12 | 14.66 | 14.66
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 850/680/595 | 1100/880/770 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260
| Noise Level(Hi/Mi/Lo) | dB(A) | 41/38/32 | 45/42/36 | 48/45/39 | 50/47/41 | 50/47/41
| Net Dimension (W*H*D) | mm | 615×615×263 | 835×835×250 | 835×835×250 | 835×835×290 | 835×835×290
| Packing Dimension (W*H*D) | mm | 700×690×330 | 900×900×330 | 900×900×330 | 900×900×370 | 900×900×370
| Net Weight | Kg | 18 | 24 | 24 | 26.5 | 26.5
| Gross Weight | Kg | 22 | 27.5 | 27.5 | 30.5 | 30.5
Panel | Net Dimension (W*H*D) | mm | 650×650×55 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55
| Packing Dimension (W*H*D) | mm | 710×710×80 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100
| Net weight | Kg | 3 | 5 | 5 | 5 | 5
| Gross weight | Kg | 5 | 7 | 7 | 7 | 7
Refrigerant Pipe | Liquid Side | mm | 6.35(1/4) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8)
| Gas Side | mm | 12.7(1/2) | 15.88(5/8) | 15.88(5/8) | 19.05(3/4) | 19.05(3/4)
| Drainage | mm | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20)
| Max. Refrigerant Pipe Length | m | 20 | 30 | 30 | 50 | 50
| Max. Difference In Level | m | 15 | 15 | 20 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm3 | 3×1mm3
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×2.5mm2 | 5×1.5mm3 | 5×1.5mm3
| Signal Wiring | mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | YKR-L/300E | YKR-L/300E | YKR-L/300E | YKR-L/300E | YKR-L/300E
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 57/120/144 | 39/76/96 | 30/70/76 | 26/54/54 | 26/54/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## R410a-T1-50Hz(CF)
Model | Indoor |  | ALCF-H18/4DR1 | ALCF-H24/4DR1 | ALCF-H36/4DR1 | ALCF-H48/5DR1 | ALCF-H60/5DR1
| Outdoor |  | AL-H18/4DR1(U) | AL-H24/4DR1(U) | AL-H36/4DR1(U) | AL-H48/5DR1(U) | AL-H60/5DR1(U)
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3
Capacity | Cooling | Btu/h | 20000-18000-5500 | 26500-24000-7200 | 40000-36000-10800 | 51800-48000-14400 | 63000-60000-18000
|  | W | 5610-5100-1530 | 7920-7200-2160 | 11000-10000-3000 | 15120-14000-4200 | 16800-16000-4800
| Heating | Btu/h | 20140-19000-4750 | 29700-27000-6750 | 43125-37500-11250 | 56100-51000-17850 | 69300-63000-22050
|  | W | 5936-5600-1400 | 8690-7900-1975 | 13225-11500-3450 | 17050-15500-5425 | 19800-18000-6300
Electric Data | Rated Cooling Power Input | kW | 2053-1579-474 | 2880-2215-665 | 4012-3086-926 | 5582-4294-1288 | 6479-4984-1495
| Rated Heating Power Input | kW | 2011-1547-464 | 2813-2164-649 | 4118-3168-950 | 5461-4201-1260 | 6429-4945-1484
| Rated Cooling Current | A | 9.81-7.55-2.25 | 13.78-10.60-3.21 | 19.19-14.77-4.45 | 9.84-7.57-2.27 | 11.18-8.60-2.57
| Rated Heating Current | A | 9.62-7.40-2.20 | 13.44-10.36-3.11 | 19.71-15.16-4.55 | 9.68-7.45-2.23 | 10.95-8.42-2.54
Performance | EER | W/W | 3.23 | 3.25 | 3.24 | 3.26 | 3.21
| COP | W/W | 3.62 | 3.65 | 3.63 | 3.69 | 3.64
Indoor Fan Fotor | Model |  | YSK-40W-4 | YSK-70W-4 | YSK-70W-4 | YSK-105W-4 | YSK-105W-4
| Brand |  | Weiling | Weiling | Weiling | Weiling | Weiling
| Output Power x Fan quantity | W | 40x1 | 70x1 | 70x1 | 105 | 105
| Capacitor | uF | 2.5 | 4 | 4 | 5 | 4
| Speed (Hi/Mi/Lo) | r/min | 1250/1100/900 | 1386/1108/970 | 1386/1108/970 | 1387/1108/970 | 1387/1108/970
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 22×19.05 | 20.5×12.7 | 22×19.05
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.and Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved
| f.Coil Length x Height x Width | mm | 599×246×38.1 | 950×246×38.1 | 950×242×57.15 | 1300×246×38.1 | 1300×242×57.15
| g.Heat Exchanging Area | m2 | 6.3 | 10 | 15.02 | 13.69 | 20.55
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 850/680/595 | 1200/960/840 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260
| Noise Level(Hi/Mi/Lo) | dB(A) | 43/40/34 | 46/43/38 | 50/47/41 | 51/48/42 | 51/48/42
| Net Dimension (W*H*D) | mm | 930×660×205 | 1280×660×205 | 1280×660×205 | 1631×660×205 | 1630×660×205
| Packing Dimension (W*H*D) | mm | 1010×720×290 | 1360×720×280 | 1360×720×280 | 1710×720×290 | 1710×720×290
| Net Weight | Kg | 25 | 32 | 33 | 44 | 44
| Gross Weight | Kg | 28 | 37 | 38 | 50 | 50
Refrigerant Pipe | Liquid Side | mm | 6.35(1/4) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8)
| Gas Side | mm | 12.7(1/2) | 15.88(5/8) | 15.88(5/8) | 19.05(3/4) | 19.05(3/4)
| Drainage | mm | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20)
| Max. Refrigerant Pipe Length | m | 20 | 30 | 30 | 50 | 50
| Max. Difference In Level | m | 15 | 15 | 20 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm3 | 3×1mm3
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×2.5mm2 | 5×1.5mm3 | 5×1.5mm3
| Signal Wiring | mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | YKR-L/300E | YKR-L/300E | YKR-L/300E | YKR-L/300E | YKR-L/300E
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 54/115/142 | 50/100/124 | 40/84/96 | 24/50/53 | 24/50/53

## R410a-T1-50Hz(MD)
Model | Indoor |  | ALMD-H18/4DR1 | ALMD-H24/4DR1 | ALMD-H36/4DR1 | ALMD-H48/5DR1 | ALMD-H60/5DR1
| Outdoor |  | AL-H18/4DR1(U) | AL-H24/4DR1(U) | AL-H36/4DR1(U) | AL-H48/5DR1(U) | AL-H60/5DR1(U)
Power Supply |  | V~,Hz,Ph | 220-240/50/1 | 220-240/50/1 | 220-240/50/1 | 380-415/50/3 | 380-415/50/3
Capacity | Cooling | Btu/h | 20000-18000-5500 | 26500-24000-7200 | 40000-36000-10800 | 51800-48000-14400 | 63000-60000-18000
|  | W | 5610-5100-1530 | 7920-7200-2160 | 11000-10000-3000 | 15120-14000-4200 | 16800-16000-4800
| Heating | Btu/h | 20140-19000-4750 | 29700-27000-6750 | 43125-37500-11250 | 56100-51000-17850 | 69300-63000-22050
|  | W | 5936-5600-1400 | 8690-7900-1975 | 13225-11500-3450 | 17050-15500-5425 | 19800-18000-6300
Electric Data | Rated Cooling Power Input | kW | 2053-1579-474 | 2880-2215-665 | 4012-3086-926 | 5582-4294-1288 | 6479-4984-1495
| Rated Heating Power Input | kW | 2011-1547-464 | 2813-2164-649 | 4118-3168-950 | 5461-4201-1260 | 6429-4945-1484
| Rated Cooling Current | A | 9.81-7.55-2.25 | 13.78-10.60-3.21 | 19.19-14.77-4.45 | 9.84-7.57-2.27 | 11.18-8.60-2.57
| Rated Heating Current | A | 9.62-7.40-2.20 | 13.44-10.36-3.11 | 19.71-15.16-4.55 | 9.68-7.45-2.23 | 10.95-8.42-2.54
Performance | EER | W/W | 3.23 | 3.25 | 3.24 | 3.26 | 3.21
| COP | W/W | 3.62 | 3.65 | 3.63 | 3.69 | 3.64
Indoor Fan Fotor | Model |  | YSK160-4 | YSK160-4 | YSK180-4 | YSK180-4 | YSK180-4
| Brand |  | Sanxiang/Weiling | Sanxiang/Kangbao | Kangbao | Kangbao | Kangbao
| Output Power x Fan quantity | W | 100 | 160 | 180 | 180 | 180
| Capacitor | uF | 3 | 2.5 | 6 | 6 | 6
| Speed (Hi/Mi/Lo) | r/min | 910/860/840 | 1050/1000/910 | 1200/1120/1060 | 1200/1120/1060 | 1200/1120/1060
Indoor Coil | a.Number Of Row |  | 2 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Spacing | mm | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.and Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 625×369×25.4 | 625×369×38.1 | 625×369×38.1 | 985×369×38.1 | 985×369×38.1
| g.Heat Exchanging Area | m2 | 6.98 | 9.87 | 9.87 | 15.56 | 15.56
Indoor Unit | Indoor Air Flow | m3/h | 950/760/665 | 1200/960/840 | 1500/1200/1050 | 2000/1600/1400 | 2000/1600/1400
| Noise Level | dB(A) | 44/41/35 | 47/44/38 | 50/47/41 | 53/50/44 | 53/50/44
| External Static Pressure | Pa | 50/80 | 50/80 | 50/80 | 50/80 | 50/80
| Net Dimension (W*H*D) | mm | 890×785×290 | 890×785×290 | 890×785×290 | 1250×785×290 | 1250×785×290
| Packing Dimension (W*H*D) | mm | 1100×870×360 | 1100×870×360 | 1100×870×360 | 1460×870×360 | 1460×870×360
| Net Weight | Kg | 34 | 36 | 36 | 52 | 52
| Gross Weight | Kg | 40 | 42 | 42 | 59 | 59
Refrigerant Pipe | Liquid Side | mm | 6.35(1/4) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8) | 9.52(3/8)
| Gas Side | mm | 12.7(1/2) | 15.88(5/8) | 15.88(5/8) | 19.05(3/4) | 19.05(3/4)
| Drainage | mm | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20) | R3/4in(DN20)
| Max. Refrigerant Pipe Length | m | 20 | 30 | 30 | 50 | 50
| Max. Difference In Level | m | 15 | 15 | 20 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24 | 16~49/-15~24
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm3 | 3×1mm3
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×2.5mm2 | 5×1.5mm3 | 5×1.5mm3
| Signal Wiring | mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | XK-02 | XK-02 | XK-02 | XK-02 | XK-02
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 42/90/111 | 42/90/108 | 36/72/87 | 21/44/50 | 21/44/50